## Hoja1
IGNEIS 10 Modular Boiler Automation
CALCULATION TABLE FOR FUEL SAVINGS
Write operational data in the fields marked with blue:
CUSTOMER: |  | MASCO - Mexico City
BOILER DATA
Nominal power |  | 900 | BHP | 8829 | kJ/s
Operating pressure |  | 7 | bar
Atmospheric pressure |  | 750 | mbar
Absolute pressure |  | 7.75 | bar
Enthalpy of steam |  | 2764.9825 | kJ/kg
Average boiler load |  | 100%
Feed water temperature |  | 70 | ºC
Enthalpy of feed water |  | 293.3 | kJ/kg
Average steam flow |  | 3.5721 | kg/s | 12859.4185 | kg/h
Actual boiler efficiency |  | 82%
Average energy consumption |  | 10767.0732 | kJ/s
Operating hours per day |  | 24 | h
Operating days per year |  | 350 | d
Operating hours per year |  | 8400 | h
FUEL CONSUMPTION AND SAVINGS
Write required information into the blue fields. Minimum possible saving with the IGNEIS 10 system is 5%, when all optimization modules are installed.
BUNKER OIL (IFO6)
Average heating value |  | 42500 | kJ/kg
Density at 25°C |  | 0.97 | kg/l
Average fuel consumption rate |  | 0.25334 | kg/s | 912.0344 | kg/h | 21888.8264 | kg/day | 7661089.2396 | kg/year
|  | 0.26118 | l/s | 940.2417 | l/h | 22565.8004 | l/day | 7898030.1439 | l/year
Price per liter |  | 0.4 | $/l
Fuel cost rate |  | 0.10447 | $/s | 376.0967 | $/h | 9026.3202 | $/day | 3159212.0576 | $/year
Minimum possible savings (percentage) |  | 5%
Anual savings |  | 157960.6029
DIESEL OIL ( IFO 2)
Average heating value |  | 43100 | kJ/kg
Density at 25°C |  | 0.83 | kg/l
Average fuel consumption rate |  | 0.24982 | kg/s | 899.3379 | kg/h | 21584.1096 | kg/day | 7554438.3453 | kg/year
|  | 0.30098 | l/s | 1083.5396 | l/h | 26004.9513 | l/day | 9101732.9462 | l/year
Price per liter |  | 0.5 | $/l
Fuel cost rate |  | 0.15049 | $/s | 541.7698 | $/h | 13002.4756 | $/day | 4550866.4731 | $/year
Minimum possible savings (percentage) |  | 5%
Anual savings |  | 227543.3237
NATURAL GAS
Average heating value |  | 40080 | kJ/Nm3
Density at 0°C |  | 0.77 | kg/Nm3
Average fuel consumption rate |  | 0.26864 | Nm3/s | 967.1024 | Nm3/h | 23210.4571 | Nm3/day | 8123659.9971 | Nm3/year
|  | 0.010767 | GJ/s | 38.7615 | GJ/h | 930.2751 | GJ/day | 325596.2927 | GJ/year
Price per energy unit (GJ) |  | 4.53 | $/GJ
Fuel cost rate |  | 0.048775 | $/s | 175.5894 | $/h | 4214.1463 | $/day | 1474951.2059 | $/year
Minimum possible savings (percentage) |  | 5%
Anual savings |  | 73747.5603
LPG
Average heating value |  | 46100 | kJ/kg
Density at 25°C |  | 0.553 | kg/l
Average fuel consumption rate |  | 0.23356 | kg/s | 840.8127 | kg/h | 20179.5037 | kg/day | 7062826.3055 | kg/year
|  | 0.42235 | l/s | 1520.4569 | l/h | 36490.9652 | l/day | 12771837.8038 | l/year
Price per liter |  | 0.38 | $/l
Fuel cost rate |  | 0.16049 | $/s | 577.7736 | $/h | 13866.5668 | $/day | 4853298.3654 | $/year
Minimum possible savings (percentage) |  | 5%
Anual savings |  | 242664.9183
Date: | 2015-03-12
AUTING CONTROL
www.auting-control.com